## Slide 1: MIDS Calculator Introduction

## Slide 2: Outline
Bioretention/BioInfiltration (w/out underdrain)
  Introduction
  Exercise 1
Bioretention/BioInfiltration with Underdrain (underdrain at bottom—biofiltration and underdrain suspended from bottom)
  Introduction
  Exercise 2

## Slide 3: Outline
Swales
  Introduction
  Exercise 3
Exercise 4: Individual vs. Clumping of BMPs
Introduce Green Roof and Permeable Pavement
Exercise 5: Several BMPs in series

## Slide 4: Opening the MIDS Calculator

## Slide 6
File saves as an excel file
Excel file contains all of the data and equations used in the calculator
Excel file can be used as a stand alone calculator

## Slide 8: Bioretention Basin Example:
Parking Lot
(1.4 acres)
Building
(0.8 acres)
Bioretention
Basin
Turf Area
(B soils,
0.8 acres)
Total site area = 3 acres

## Slide 10
Performance goal
(1.1 inches * Impervious Area)
Drag and Drop
Bioretention Icon

## Slide 11
Double Click
Or
Right Click and select
Edit Properties

## Slide 17: Design Requirements for Bioretention Basins
Overflow depth cannot be > 1.5 feet
Basin must meet drawdown time requirement (48 or 24 hours)
Infiltration rate cannot be > 1.63 inches/hour (this is being examined and might change)
Bottom surface area cannot be greater than overflow surface area

## Slide 21: Annual Pollutant Load Reduction Calculations
Calculate Annual Pollutant load to BMP
  Calculate annual TP and TSS pollutant load from direct watershed
  Add any remaining TP/TSS loads from upstream BMPs

## Slide 22: Annual Pollutant Load Reduction Calculations
% Annual Volume Reduction?
% Annual Volume Overflow?

## Slide 23: Performance Curve for Type B soils (0.3 in/hr)
Chart: BMP Volume (ft3)
| 0 | 150 | 300 | 450 | 599.09999999999991 | 1197.9000000000001 | 1797 | 2395.8000000000002 | 2994.8999999999996 | 3593.7000000000003 | 4192.8 | 4791.6000000000004 | 5390.7000000000007 | 5989.4999999999991 | 6588.6 | 7187.4000000000005 | 7786.5 | 8385.3000000000011 | 8984.4000000000015 | 9583.2000000000007 | 10781.099999999999 | 13068 | 14999.999999999996 | 19500 | 26136
0.0 | 0 | 0.24315 | 0.3916 | 0.49119 | 0.55853 | 0.70771 | 0.76898 | 0.80459 | 0.83251 | 0.85827 | 0.88269 | 0.90496 | 0.92186 | 0.93447 | 0.94747 | 0.95528 | 0.96059 | 0.96475 | 0.96817 | 0.97203 | 0.9789 | 0.98845 | 0.99283 | 0.99683 | 1
0.1 | 0 | 0.19584 | 0.32248 | 0.413 | 0.47881 | 0.64362 | 0.72648 | 0.77971 | 0.81974 | 0.85223 | 0.87968 | 0.90323 | 0.92136 | 0.93502 | 0.94766 | 0.95589 | 0.96202 | 0.96687 | 0.97083 | 0.97459 | 0.98085 | 0.98928 | 0.99311 | 0.99655 | 1
0.3 | 0 | 0.10122 | 0.18424 | 0.25661 | 0.31936 | 0.51545 | 0.64147 | 0.72996 | 0.79419 | 0.84015 | 0.87364 | 0.89976 | 0.92035 | 0.93612 | 0.94804 | 0.95712 | 0.96489 | 0.97112 | 0.97614 | 0.97973 | 0.98475 | 0.99092 | 0.99365 | 0.996 | 1
0.5 | 0 | 0.067134 | 0.12534 | 0.17842 | 0.22633 | 0.39288 | 0.51755 | 0.61237 | 0.6859 | 0.74521 | 0.79252 | 0.8308 | 0.86241 | 0.887 | 0.90666 | 0.92261 | 0.93604 | 0.94714 | 0.9562 | 0.96363 | 0.97389 | 0.98494 | 0.99025 | 0.99561 | 1
0.7 | 0 | 0.050157 | 0.094631 | 0.13608 | 0.17439 | 0.31278 | 0.42539 | 0.51721 | 0.59278 | 0.65425 | 0.7059 | 0.75021 | 0.78731 | 0.81877 | 0.84609 | 0.86916 | 0.88844 | 0.90434 | 0.91782 | 0.92932 | 0.94747 | 0.96974 | 0.98036 | 0.99174 | 1
0.9 | 0 | 0.039931 | 0.075883 | 0.10982 | 0.14153 | 0.25897 | 0.35868 | 0.44393 | 0.5167 | 0.57899 | 0.63203 | 0.67736 | 0.71695 | 0.75219 | 0.78272 | 0.80923 | 0.8325 | 0.85316 | 0.8713 | 0.88743 | 0.9122 | 0.94425 | 0.96166 | 0.98398 | 1
1.0 | 0 | 0.034818 | 0.066509 | 0.096693 | 0.1251 | 0.23207 | 0.32532 | 0.40729 | 0.47866 | 0.54137 | 0.59509 | 0.64094 | 0.68177 | 0.7189 | 0.75103 | 0.77926 | 0.80453 | 0.82757 | 0.84804 | 0.86648 | 0.89456 | 0.9315 | 0.95232 | 0.9801 | 1
BMP Volume = 8785 ft3
Impervious Area = 73%
Annual Volume Reduction = 90.5%

## Slide 24: Annual Pollutant Load Reduction
100% TSS, PP, DP Reduction
0% TSS, Particulate P (PP), and Dissolved P (DP) Reduction
91% Annual Volume
9 % Annual Volume

## Slide 25: Questions?

## Slide 26: Exercise 1: Simple Bioretention New Project on Site without Restrictions
Source: Larson Engineering

## Slide 27
Source: Larson Engineering

## Slide 28: Exercise 1: Calculator Inputs
Drainage Area | Land Cover (acres) - assume all 'B' Soils |  |  | Total
 | Turf | Forest/Open Space | Impervious | 
WEST | 5.95 | 0.00 | 2.53 | 8.48
EAST | 5.35 | 0.00 | 2.60 | 7.95
Total: | 11.3 | 0.00 | 5.13 | 16.43
Drainage Area | BMP Description | BMP Information |  | 
 |  | Overflow Surface area (ft2) | Bottom Surface Area (ft2) | Overflow Depth (ft)
WEST | Bioretention basin | 14,000 | 11,000 | 1.2
EAST | Bioretention basin | 7,500 | 5,000 | 1.2
Zip Code: 55001

## Slide 29: Exercise 1: Assignment/Questions
Does the site conform to the new site without restrictions performance goal?
What percentage of TP is removed from WEST, EAST, and Total?
How would you make this site conform to the performance goal?
Notes: You lost me on that 3rd bullet

## Slide 30: Lunch

## Slide 31: Bioretention Basin with Underdrain Example:
Parking Lot
(1.4 acres)
Building
(0.8 acres)
Bioretention
Basin with
underdrain
Turf Area
(B soils,
0.8 acres)
Total site area = 3 acres

## Slide 33: Bioretention Basin with an Underdrain

## Slide 36: Infiltration through side of BMP
Where
IR = infiltration rate (always 0.06 in/hr)
DDT = drawdown time requirement (48 or 24 hours)
AS = BMP surface area at BMP overflow
AO = surface area at underdrain
AS
AO

## Slide 38: Volume losses through Evapotranspiration
Where
AM = BMP surface area at media surface (ft2)
0.31 in/day = max pan ET rate recorded in Minnesota (Climate of Minnesota Part XII – The Hydrologic Cycle and Soil Water, 1979)
0.5 = correction factor for pan ET rate
3 days = typical time period between precipitation events (per MPCA)
D = Total media depth of BMP (ft)
DO = media depth below underdrain (ft)
(FC – WP) = water holding capacity of media (i.e., Field capacity – Wilting point)
minimal value between ET rate and the media water holding capacity
Notes: This slide has bunch of small text….can’t expect folks to be able to see it on a screen

## Slide 42: Infiltration through bottom of BMP
Where
IR = infiltration rate
(always 0.06 inches/hour)
DDT = drawdown time requirement (48 or 24 hours)
AB = surface area at bottom

## Slide 43: Annual Pollutant Load Reduction
100% TSS, PP, DP Reduction
(performance curves)
45% PP
0% DP
60% TSS

## Slide 44: Exercise 2: Bioretention Basins with Underdrains
Zip Code: 55001
Source: Larson Engineering
Bioretention basin with elevated underdrain
Bioretention basin with underdrain at the bottom
Impervious
Drainage area

## Slide 45: Exercise 2: Givens
Drainage Area | Land Cover (acres) - assume all ‘D' Soils |  |  | Total
 | Turf | Forest/Open Space | Impervious | 
WEST | 5.95 | 0.00 | 2.53 | 8.48
EAST | 5.35 | 0.00 | 2.60 | 7.95
Total: | 11.3 | 0.00 | 5.13 | 16.43
Drainage Area | BMP Description | BMP Information |  |  |  |  |  |  |  |  | 
 |  | Surface Area at Overflow (ft2) | Area at Media Surface (ft2) | Surface Area at Underdrain (ft2) | Bottom Surface Area (ft2) | Total Media Depth (ft) | Depth below Underdrain (ft) | field capacity – Wilting point (ft3/ft3) | Media porosity (ft3/ft3) | Underlying Soil | Required drawdown time (hours)
WEST | Bioretention basin with elevated underdrain | 14,000 | 11,000 | 8500 | 7875 | 1.24 | 0.24 | 0.11 | 0.3 | CL | 48
EAST | Bioretention basin with underdrain at the bottom | 7,500 | 5,000 | 2400 | 2400 | 1 | NA | 0.11 | 0.3 | CL | 48

## Slide 46: Exercise 2: Assignment/Questions
What is the annual TP reduction at WEST and EAST?

## Slide 47: Swale BMP
Swales separated into components
  Side slope
  Dry swale - main channel
  Dry swale with an underdrain - main channel
  Wet swale – main channel
Photo: Ray Roemmich
Side Slope Reductions
Bottom/Main Channel Reductions

## Slide 48
Swale Side Slope
Swale Main Channel
Swale Main Channel with Underdrain
Wet Swale

## Slide 49: Why separate components?
Swale Side Slope
Wet Swale – Main Channel
Dry Swale – Main Channel
Dry Swale w/ underdrain – Main Channel
Watershed Area
BMP overflow

## Slide 50: Swale BMP
Roadway
(0.5 acre)
Sheet Flow
Dry
Swale
27.2 feet
800 feet
Swale Side slope area: = 0.367 acres
Swale Main Channel Area: = 0.073 acres
Total Area = 0.94 acres

## Slide 58: How is swale volume reduction capacity calculated?
55 years of P8 modeling based on multiple configurations of side slope, channel length, flow path length, infiltration rate, and Manning’s n
P8 model results were used to develop relationship between swale parameters and annual volume reductions
Performance curves are used to convert annual reductions to event based reductions

## Slide 59: Look up table for type A soils (1.63 in/hr)
Chart: BMP Volume (ft3)
| 0 | 43.35 | 86.7 | 130.05000000000001 | 173.13989999999998 | 346.19310000000002 | 519.33299999999997 | 692.38620000000003 | 865.52609999999993 | 1038.5793000000001 | 1211.7192 | 1384.7724000000001 | 1557.9123 | 1730.9654999999998 | 1904.1054000000001 | 2077.1586000000002 | 2250.2984999999999 | 2423.3517000000002 | 2596.4916000000003 | 2769.5448000000001 | 3115.7378999999996 | 3776.652 | 4334.9999999999991 | 5635.5 | 7553.3040000000001
0.0 | 0 | 0.56778 | 0.77562 | 0.88519 | 0.95091 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
0.1 | 0 | 0.45259 | 0.63709 | 0.74481 | 0.81621 | 0.93806 | 0.9719 | 0.9848 | 0.99019 | 0.99302 | 0.99532 | 0.99708 | 0.99859 | 0.9992 | 0.99973 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
0.3 | 0 | 0.22222 | 0.36004 | 0.46404 | 0.54679 | 0.75223 | 0.85796 | 0.91477 | 0.94612 | 0.9648 | 0.97615 | 0.98386 | 0.9883 | 0.99106 | 0.99325 | 0.99502 | 0.99595 | 0.9965 | 0.99688 | 0.99727 | 0.99769 | 0.99849 | 0.99913 | 1 | 1
0.5 | 0 | 0.14507 | 0.24757 | 0.33191 | 0.40209 | 0.60469 | 0.72712 | 0.80583 | 0.86042 | 0.89834 | 0.92449 | 0.943 | 0.95652 | 0.96648 | 0.97359 | 0.97955 | 0.98381 | 0.98666 | 0.98886 | 0.99045 | 0.99316 | 0.99631 | 0.99705 | 0.99817 | 1
0.7 | 0 | 0.1072 | 0.1878 | 0.25678 | 0.31735 | 0.50129 | 0.62639 | 0.7135 | 0.77617 | 0.82358 | 0.86039 | 0.88915 | 0.91094 | 0.92776 | 0.94116 | 0.95171 | 0.96003 | 0.96668 | 0.97178 | 0.97637 | 0.98333 | 0.98996 | 0.99315 | 0.9967 | 1
0.9 | 0 | 0.084833 | 0.15079 | 0.20904 | 0.26111 | 0.4277 | 0.5479 | 0.63759 | 0.70506 | 0.75716 | 0.79807 | 0.83224 | 0.86011 | 0.88331 | 0.90178 | 0.9171 | 0.92947 | 0.93983 | 0.94839 | 0.95561 | 0.96665 | 0.98024 | 0.98649 | 0.9935 | 1
1.0 | 0 | 0.073651 | 0.13228 | 0.18517 | 0.23299 | 0.3909 | 0.50866 | 0.59964 | 0.6695 | 0.72395 | 0.76691 | 0.80378 | 0.8347 | 0.86109 | 0.88209 | 0.8998 | 0.91419 | 0.9264 | 0.9367 | 0.94523 | 0.95831 | 0.97538 | 0.98316 | 0.9919 | 1
Annual Percent Reduction = 24%
Impervious Area = 58%
BMP Volume = 99 ft3

## Slide 60: Calculator Requirements for Side Slopes
Can only be routed to swale main channel BMPs (swale main channel, swale main channel with an underdrain, wet swale)
Cannot receive runoff from other BMPs
Flow must be sheet flow over entire channel length (if not, channel length should be adjusted to only cover areas where sheet flow occurs)
Only calculates flow from one side slope

## Slide 61: Calculator Requirements Continued
Manning’s n cannot be > 1
Infiltration rate cannot be > 1.63 inches/hour (might change)
Side slopes cannot be steeper than 3H:1V or flatter than 7H:1V

## Slide 65
Calculated with same
method used for side slope
calculation

## Slide 66
Calculate the volume of
water that can be held behind
the check dam at any one time

## Slide 67
Total volume reduction
capacity equals the sum of
the two reductions

## Slide 68
Bioretention base volume loss
replaces channel bottom
calculation

## Slide 69: Annual Pollutant Load Reduction
100% TSS, PP, DP Reduction
(performance curves)
73% PP
0% DP
68% TSS

## Slide 70: Design Requirements
Swale bottom width cannot be < 2 feet
Channel slope cannot be > 4%
Manning’s n cannot be > 1
Water behind check dam must drain within required drawdown time (48 or 24 hours)
Infiltration rate cannot be > 1.63 inches/hour (might change)

## Slide 71: Exercise 3: Simple Swale
Rural Section of Highway 5 in Lake Elmo
Source: Minnesota Department of Transportation

## Slide 72: Exercise 3: Simple Swale
Rural Section of Highway 5 in Lake Elmo, MN (55042)
  Drainage Area A5:
    B soils
    Rectangular drainage area: 450’ by 100’
    Road/shoulder: 27’ wide
    Swale side slopes must start no closer than 5 feet from edge of pavement
    Longitudinal slope is 2%
    Side slope is 4:1

## Slide 73
27’
20’
8’
20’
25’
Roadway
100’
Swale side slope
watershed
Swale main channel
watershed

## Slide 74: Exercise 3A: Assignment/Questions
Use given swale cross-section and no check dam or bioretention base
  Determine the volume of runoff lost through the entire swale by the road with mowed turf
  with native (tall) grass
Extra time?:
  Design side slope and bottom swale and determine the effect of
    Flatter/steeper side slopes
    Wider/narrower base
    Changes in other parameters

## Slide 75: Exercise 3B: Add a stormwater pond
Assume an adjacent stormwater pond discharges into the bottom of the swale

## Slide 76: Exercise 3B: Givens
Stormwater Pond drainage area (designed to specific standards):
  0.45 acres of B soils in turf
  0.25 acres of impervious surface

## Slide 77: Exercise 3B: Assignment/Questions
Does the example conform to the performance goal?
What percent annual TSS is removed?

## Slide 78: Exercise 3C: Assignment/Question
Add check dams and a bioretention base until the example conforms to the performance goal. What did you do?

## Slide 79: Exercise 4: “Individual” vs. “Clumping”
Source: Original from Folz, Freeman, and Erickson and modified for this exercise by Barr Engineering
Site’s zip code: 55042

## Slide 80: Exercise 4A: “Individual” Givens

## Slide 81: Exercise 4B: “Clumping” Givens

## Slide 82: Exercise 4: Assignment/Questions
Determine the results by calculating bioretention basins with individual drainage areas and as one clumped basin.
Are the results different? Why/why not?
Extra Time?:
Experiment with the “Individual” routing to optimize the volume retention.

## Slide 83: Permeable Pavement
Parking Lot
(0.8 acres)
Permeable Pavement
(0.8 acres)
Turf Area (B soils,0.4 acres)
Total Area = 2 acres

## Slide 84
Permeable pavement area
is treated as Impervious area.

## Slide 88
If BMP reduction capacity is greater than required treatment volume, BMP only receives credit equal to required treatment volume

## Slide 89: Annual Pollutant Load Reduction
100% TSS, PP, DP Reduction
(performance curves)
82% PP
0% DP
74% TSS

## Slide 90: Design Requirements
Ratio between total impervious area and permeable pavement surface area cannot exceed 5:1
Must meet drawdown time requirement (48 or 24 hours)
Infiltration rate cannot > 1.63 inches/hour (might be changed)

## Slide 91: Green Roof
Roof Area
0.25 acres
Green roof area
(0.25 acres)
Total Area
0.50 acres

## Slide 94
Can only enter impervious area into watershed area for green roof
Green roof area is included as impervious cover

## Slide 97: Annual Pollutant Load Reduction
Zero TP load reduction even through volume loss
Outflow TSS EMC (event mean concentration) always equal to 2.25 mg/l.

## Slide 98: Design Requirements & Water Quality Note
Green roof media depth cannot be > 4 inches
Green roof area cannot be greater than the total impervious area routed to the green roof
Total impervious area (other contributing areas + green roof area) to green roof area ratio cannot exceed 2:1
Green roofs do not provide phosphorus load reduction

## Slide 99: Non-Volume Reduction BMPs
Calculated from performance curves

## Slide 100: Exercise 5: Several BMPs in Series
Zip Code: 55418

## Slide 101: Exercise 5: Givens

## Slide 102: Exercise 5: Givens

## Slide 103: Exercise Steps
Enter Site information
Put all 6 BMPs into schematic window
Route all BMPs
Start entering BMP information.

## Slide 104: Exercise 5: Assignment/Questions
Does the site meet the performance goal for new sites without restrictions?
Are any BMPs oversized or undersized?
Extra Time?:
Modify BMPs to optimize design (volume retention).